## Inspection Events by Facility
Fort Wayne City Utilities | Filter Criteria: Inspection Events Only | All Permits All Inspection Events Due Date: Sep 1 2025 - Apr 22 2026 | Fats, Oils and Grease Program | Inspection Event Details - Inspection Report
txtPermitInfo | ContactType | Text108 | Text112 | txtDueDate | Text102 | Text104 | Text106 | txtInspectMaintLog | Text105 | Text115 | txtOtherPersonPresent | txtInspectReason | txtEventDesc | Text117 | Text110
[9199] A Divine Encounter Café - 1019 E. Coliseum Blvd. Coliseum Blvd., E., 1019 Fort Wayne
| Bogus Event - made up description |  |  | 2025-10-09 | COS | 2025-10-09 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed functional condition no evidence of corrosion |  | No
| informational - lowercased on purpose |  |  | 2025-10-09 | COS | 2025-10-09 | COS | - | - |  |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained explained cleaning requirements and log |  | No
[8073] Agaves Mexican Grill Maysville - 10460 Maysville Rd. Maysville Rd., 10460 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility This facility will now be put on our sampling list. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed The grease interceptor is shared with Subway |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH is shared between Agave's and Subway |  | No
[8073] Agaves Mexican Grill Maysville - 10460 Maysville Rd. Maysville Rd., 10460 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1517] Agaves Mexican Grill Washington - 212 E. Washington Ctr. Rd. Washington Ctr. Rd., E., 212 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[1517] Agaves Mexican Grill Washington - 212 E. Washington Ctr. Rd. Washington Ctr. Rd., E., 212 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | - | Hazael Molina |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9484] Alberto's Mexican Grill - 2529 S. Calhoun St. Calhoun St., S., 2529 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE is open from 10am to 10 pm carry out only. No grease trap or sampling port present at the facility. Owner was informed to have a licensed plumber install both, |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - | Adalberto Marinez |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17854] Allen County Community Corrections Residential Services Facillity - 7117 Venture Ln. Venture Ln., 7117 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-09-10 | COS | 2025-09-10 | COS | - | - |  |  | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator all kitchen fixtures except DW |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-09-10 | COS | 2025-09-10 | COS | - | - |  |  | Remodel | A dye trace to prove the monitoring point belongs to the facility. Done at dishwasher (DW). |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-10 | COS | 2025-09-10 | COS | - | - |  |  | Remodel follow-up | A grease trap/interceptor inspection performed Rings and plugs removed and castings installed. Center baffle in place. Outlet tee/downleg needs installed and send photos. |  | No
[1011] Amay Kitchen - 3620 N. Clinton St. Clinton St., N., 3620 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-06 | MAR | 2025-11-06 | MAR | - | - | Min Aung |  | Existing facility | Inspection to collect information or data about the facility FSE was informed to have a licensed plumber inspect and install a sampling port. FSE representative was very frustrated with this and initially refused to sign Inspection report. He insisted th |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-06 | MAR | 2025-11-06 | MAR | - | PASS - Passed Inspection | Min Aung |  | Existing facility | A grease trap/interceptor inspection performed Grease trap had recently been cleaned. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-06 | MAR | 2025-11-06 | MAR | - | - | Min Aung |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9927] Amaya - 1734 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1734 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-17 | MAR | 2025-11-17 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Hemang Patel |  | Existing facility | A grease trap/interceptor inspection performed Grease trap needed cleaned. FSE was asked to send pictures when down. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-17 | MAR | 2025-11-17 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-17 | MAR | 2025-11-17 | MAR | - | - | Hemang Patel |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9927] Amaya - 1734 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1734 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Verify that they did the 30 day maintenance was completed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[18080] Amazon.com Services LLC - FWA6 - 5510 Flaugh Rd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-02-19 | COS | 2026-02-19 | COS | - | - |  | Brenda Stopher | Complaint | Inspection to collect information or data about the facility Inspection from a grease backup complaint that lead to a storm water illicit discharge. Looked at the breakrooms on each floor as well ad the main cafeteria area, all mop sinks and the recruiti |  | No
[18080] Amazon.com Services LLC - FWA6 - 5510 Flaugh Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-19 | COS | 2026-02-19 | COS | - | - |  | Brenda Stopher | Complaint | Monitoring point inspection evidence of a backup 15' deep in the 17' deep manhole |  | No
| Complaint/Investigation - Complaint (IDEM, DOH, WPCM, WPCP, Facility, or Misc.) |  |  | 2026-02-20 | COS | 2026-02-20 | COS | - | - |  | Brenda Stopher | Grease backup and Illicit storm water discharge | Complaint (IDEM, DOH, WPCM, WPCP, Facility, or Misc.) Email to WPCM: Brenda and I investigated last week. We walked through the whole facility and inspected their cleaning areas and their kitchen spaces. We found little evidence of dumping. We determi |  | No
[18443] American Kolache - 6405 Lima Rd. Lima Rd., 6405 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-09-12 | COS | 2025-09-12 | COS | - | - |  |  | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator Sampling port directly after grease trap |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-12 | COS | 2025-09-12 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed Grease trap has all components in place. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-12 | COS | 2025-09-12 | COS | - | - |  |  | Remodel | Monitoring point inspection Sampling Port directly after grease trap |  | No
[7666] Applebee's - 5414 Meijer Dr. Meijer Dr., 5414 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17588] Arby's #8118 - 10112 Maysville Rd. Maysville Rd., 10112 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17312] Auntie Anne's - In Meijer - 10301 Maysville Rd Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease trap was overly full |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH is shared with Meijer |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18421] Auntie Annes's in Meijer - 4242 E. Dupont Rd. Ste. B Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-12-17 | COS | 2025-12-17 | COS | - | - |  | Leah | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator confirmed all kitchen fixtures flow to the grease interceptor |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-17 | COS | 2025-12-17 | COS | - | - |  | Leah | Remodel | A grease trap/interceptor inspection performed functional condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-17 | COS | 2025-12-17 | COS | - | - |  | Leah | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18470] Axe to Grind - 909 N. Coliseum Blvd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-21 | COS | 2025-11-21 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed Both in functional/new condition with all components in place. There's also an inlet basket in each grease trap |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-21 | COS | 2025-11-21 | COS | - | - |  |  | Remodel | Monitoring point inspection functional/new condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-21 | COS | 2025-11-21 | COS | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9893] B. Antonio's Pizza - 5417 Meijer Dr. Meijer Dr., 5417 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | PASS - Passed Inspection | Alicia Warner |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH inspected is in the grass east of the FSE. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | PASS - Passed Inspection | Alicia Warner |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[6385] Baba's #25 Inc. - 7505 S. Anthony Blvd. Anthony Blvd., S., 7505 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | PASS - Passed Inspection | Moe Rafati | Leah | Existing facility | Inspection to collect information or data about the facility FSE was inspected for CMH and Grease trap. CMH is functional and on the north side of the drive thru. Grease trap is above floor by the 3 basin sink and is functional |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | PASS - Passed Inspection | Moe Rafati | Leah | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | PASS - Passed Inspection | Moe Rafati | Leah | Existing facility | Monitoring point inspection |  | No
[6385] Baba's #25 Inc. - 7505 S. Anthony Blvd. Anthony Blvd., S., 7505 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | - | Moe Rafati | Leah | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9388] Banh Mi Pho Shop - 1925 Fairfield Ave. Fairfield Ave., 1925 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-06 | COS | 2025-10-06 | COS | - | - |  |  | Mod Check | Inspection to collect information or data about the facility The dishwasher has been replumbed to bypass the grease trap. They have very limited space so they may not be able to reasonably install a sampling port in the future |  | No
[9287] Bernie Best Deal Store - 1411 N. Coliseum Blvd. Coliseum Blvd., N., 1411 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-12 | COS | 2025-09-12 | COS | - | - |  |  | Remodel Follow Up | A grease trap/interceptor inspection performed confirmed that the grease trap has not been moved. Received inspection request from DVS stating that the GT was in the basement which is not what we had in our files. Confirmed that this is incorrect and the |  | No
[9732] Biaggi's Ristorante Italiano - 4010 W. Jefferson Blvd. Jefferson Blvd., W., 4010 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Matthew Doehrmann |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor needs pumped for inspection |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Matthew Doehrmann |  | Existing facility | Monitoring point inspection Sanitary and grease in trench |  | No
[9732] Biaggi's Ristorante Italiano - 4010 W. Jefferson Blvd. Jefferson Blvd., W., 4010 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | - | Matthew Doehrmann |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[5834] Big Eyed Fish - 1502 N. Wells St. Wells St., N., 1502 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-05 | MAR | 2025-11-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-05 | MAR | 2025-11-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17506] BJ's Restaurant (CUGC) - 245 W. Coliseum Blvd. Coliseum Blvd., W., 245 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | - | Elizabeth Darnell |  | Existing facility | Inspection to collect information or data about the facility CMH is offset so a sampler will not fit and the CMH is in the middle of the driveway. Grab samples only can be taken at this FSE. Grease interceptor is a 2 hole model and had recently been pum |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | PASS - Passed Inspection | Elizabeth Darnell |  | Existing facility | A grease trap/interceptor inspection performed External grease Interceptor is a 2 hole model |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | PASS - Passed Inspection | Elizabeth Darnell |  | Existing facility | Monitoring point inspection CMH is functional for a grab sample |  | No
[17506] BJ's Restaurant (CUGC) - 245 W. Coliseum Blvd. Coliseum Blvd., W., 245 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | - | Elizabeth Darnell |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9554] Bob Evans Restaurant #318 - 2935 E. Dupont Rd. Dupont Rd., E., 2935 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor was overly full and I was unable to see the center baffle |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[9554] Bob Evans Restaurant #318 - 2935 E. Dupont Rd. Dupont Rd., E., 2935 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[7667] Bob Evans Restaurant #456 - 5135 Meijer Dr. Meijer Dr., 5135 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | - | Paige Carnahan |  | Existing facility | Inspection to collect information or data about the facility While discussing the condition of the Grease Interceptor and the CMH, the manager informed me that they often get sewer smell and water coming up in the drain in the kitchen. |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Paige Carnahan |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor was over full and FSE was informed to have it pumped and jetted. |  | No
[7667] Bob Evans Restaurant #456 - 5135 Meijer Dr. Meijer Dr., 5135 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Paige Carnahan |  | Existing facility | Monitoring point inspection CMH had a considerable amount of foreign material hanging up inside it |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | - | Paige Carnahan |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2026-02-11 | COS | 2026-02-11 | COS | - | - |  |  | Pumpout | Inspection to collect information or data about the facility the interceptor needs replaced or repaired. The CMH should be replaced or repaired due to a belly in the line. Will be sending letter because management was not present during inspection |  | No
[7667] Bob Evans Restaurant #456 - 5135 Meijer Dr. Meijer Dr., 5135 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-11 | COS | 2026-02-11 | COS | - | - |  |  | Pumpout | A grease trap/interceptor inspection performed saw the interceptor empty. There is rebar exposed along all the walls, the bottom and the baffles. The inlet baffle is half corroded |  | No
[18469] Bon Bon's Coffee - 5712 Maplecrest Rd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility This facility had not been inspected in a while and it has a hand sink, low temp dishwasher, pre wash sink, mop sink, and another single basin sink. The FSE was informed to have a licensed plum |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0032] Botanical Gardens Café - 1100 S. Calhoun St. Calhoun St., S., 1100 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-30 | COS | 2025-09-30 | COS | - | - |  |  | Remodel | Inspection to collect information or data about the facility Shelving is over the grease trap and they will have to move the shelving every time they need to clean. They said they are ok with this |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-30 | COS | 2025-09-30 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed Existing grease trap (1) functional. Required cleaning every two weeks and keep log of cleanings. Grease trap needs to be accessible - shelving units over grease trap lid needs to be removable |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-30 | COS | 2025-09-30 | COS | - | - |  |  |  | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18488] Bowen Coffee Shop - 201 E. Rudisill Blvd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-04-13 | MAR | 2026-04-13 | MAR | - | - |  |  | Remodel | Inspection to collect information or data about the facility FSE was inspected and dye traced. FSE is not plumbed according to plan, so it could not be signed off. The 3 basin sink goes to Grease trap but nothing else currently does and it all should be. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-13 | MAR | 2026-04-13 | MAR | - | PASS - Passed Inspection |  |  | Remodel | A grease trap/interceptor inspection performed Zurn Grease Interceptor is in the floor in the basement |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-13 | MAR | 2026-04-13 | MAR | - | PASS - Passed Inspection |  |  | Remodel | Monitoring point inspection Sampling port is in the basement in the floor |  | No
[18488] Bowen Coffee Shop - 201 E. Rudisill Blvd. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-13 | MAR | 2026-04-13 | MAR | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained Outreach packet was left with Contractor. One will need to be giving to FSE operator. |  | No
[18459] Bubba's 33 - 317 E. Coliseum Blvd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-10-27 | COS | 2025-10-27 | COS | - | - |  | Jeffrey Osborne | New Build | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator all kitchen fixtures except high-temp dishwasher and the low temp dishwasher behind the bar to grease |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-10-27 | COS | 2025-10-27 | COS | - | - |  | Jeffrey Osborne | New Build | A dye trace to prove the monitoring point belongs to the facility The dishwashers flow to the CMH |  | No
[18459] Bubba's 33 - 317 E. Coliseum Blvd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-27 | COS | 2025-10-27 | COS | - | - |  | Jeffrey Osborne | New Build | A grease trap/interceptor inspection performed Functional/new condition with inlet and outlet tees/down-legs |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-27 | COS | 2025-10-27 | COS | - | - |  | Jeffrey Osborne | New Build | Monitoring point inspection functional condition. Existing manhole which was offset. Can do grab sample only |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-27 | COS | 2025-10-27 | COS | - | - |  | Jeffrey Osborne | New Build | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[8071] Buffalo Wild Wings - 10524 Maysville Rd. Maysville Rd., 10524 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Recommend Grease Interceptor be pumped |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1177] Buffalo Wings and Ribs - 4636 Coldwater Rd. Coldwater Rd., 4636 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-12 | COS | 2025-09-12 | COS | - | - |  |  | Mod check | A grease trap/interceptor inspection performed new interceptor is in the same location as the old one that was removed. It is a 2 MH interceptor and has a center baffle and outlet tee/downleg in place. |  | No
[18462] Burger Bar - 223 W. Jefferson Blvd. Ste. 150 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-28 | SJR | 2025-10-28 | SJR | - | - |  | Mark A Rekeweg | Existing facility | A grease trap/interceptor inspection performed Could only open 1 lid to GT bc a temporary construction dumpster was over the other lid. GT was full and all parts appeared to be in working order. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-28 | SJR | 2025-10-28 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | Monitoring point inspection CMH appears to be in working condition No steps in place |  | No
[18462] Burger Bar - 223 W. Jefferson Blvd. Ste. 150 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-28 | SJR | 2025-10-28 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | Outreach to a facility manager where an outreach binder is delivered & explained Confirmed that they share a GT and CMH with the Hampton Inn and Connor's Rooftop Bar. |  | No
[9298] Burger II Dairy Mart - 1450 St. Joseph Blvd. St. Joe Blvd., 1450 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-30 | COS | 2025-10-30 | COS | - | - |  | Noah Crouse | Existing Facility | Inspection to collect information or data about the facility facility does not use the sinks. They do not wash the drip trays of the coffee machines (only wipe up with paper towels). No other cooking, prepping or washing occurs |  | No
[9288] Burger's Inc. - 1412 N. Wells St. Wells St., N., 1412 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-05 | MAR | 2025-11-05 | MAR | - | PASS - Passed Inspection | Kanwaljeeb Kaur |  | Existing facility | Inspection to collect information or data about the facility FSE is a mini mart that only offers pre packaged foods. FSE was informed if in the future food is prepared or containers cleaned on site that a grease trap and a sampling port would be require |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-05 | MAR | 2025-11-05 | MAR | - | PASS - Passed Inspection | Kanwaljeeb Kaur |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17277] Captain Ron's - 4530 Bluffton Rd. Bluffton Rd., 4530 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Remodel | Inspection to collect information or data about the facility Determine what is present and if they can do a sampling port. They would have room to do a sampling port if the switched around plumbing |  | No
[17277] Captain Ron's - 4530 Bluffton Rd. Bluffton Rd., 4530 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed Grease trap, 3 basin is new No sampling location in place 3 basin is the only dish area No sanitary clean outs present |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0040] Carriage House - 3327 Lake Avenue Lake Ave., 3327 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-18 | MAR | 2025-11-18 | MAR | - | - | Nick Doehrman |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[0040] Carriage House - 3327 Lake Avenue Lake Ave., 3327 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-18 | MAR | 2025-11-18 | MAR | - | - | Alexander Wilson |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[8231] Casa Grille - 411 E. Dupont Rd. Dupont Rd., E., 411 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[8231] Casa Grille - 411 E. Dupont Rd. Dupont Rd., E., 411 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[7720] Casa Grille Italiano - 6340 Stellhorn Rd. Stellhorn Rd., 6340 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-06 | MAR | 2026-03-06 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-06 | MAR | 2026-03-06 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[7720] Casa Grille Italiano - 6340 Stellhorn Rd. Stellhorn Rd., 6340 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-06 | MAR | 2026-03-06 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[531] Cebolla's Mexican Grill - 2787 Maplecrest Rd. Maplecrest Rd., 2787 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[531] Cebolla's Mexican Grill - 2787 Maplecrest Rd. Maplecrest Rd., 2787 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-02 | MAR | 2026-02-02 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10061] Champ's Nashville Hot Chicken 2 - 6328 E. State Blvd. State Blvd., E., 6328 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-12 | MAR | 2025-11-12 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Chris Hoeppner |  | Existing facility | A grease trap/interceptor inspection performed Grease trap baffle is rusted out and will need replaced. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-12 | MAR | 2025-11-12 | MAR | - | - | Chris Hoeppner |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17663] Chick-fil-A #03479 - 182 W. Coliseum Blvd. Coliseum Blvd., W., 182 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Facility was inspected and the CMH passed and the Grease Interceptors passed. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | PASS - Passed Inspection | Zach Gladieux |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | PASS - Passed Inspection | Zach Gladieux |  | Existing facility | Monitoring point inspection |  | No
[17663] Chick-fil-A #03479 - 182 W. Coliseum Blvd. Coliseum Blvd., W., 182 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9187] China Express - 1003 W. Coliseum Blvd. Coliseum Blvd., W., 1003 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | Monitoring point inspection Needs jetted and cleaned due to grease build up |  | No
[9187] China Express - 1003 W. Coliseum Blvd. Coliseum Blvd., W., 1003 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[5831] Chipotle Mexican Grill #1066 - 910 E. Coliseum Blvd. Coliseum Blvd., E., 910 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-03 | MAR | 2026-02-03 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-03 | MAR | 2026-02-03 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[5831] Chipotle Mexican Grill #1066 - 910 E. Coliseum Blvd. Coliseum Blvd., E., 910 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-03 | MAR | 2026-02-03 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17406] Chipotle Mexican Grill #2691 - 6175 Lima Rd. Lima Rd., 6175 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[17406] Chipotle Mexican Grill #2691 - 6175 Lima Rd. Lima Rd., 6175 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[4397] Chung King Express - 3101 N. Anthony Blvd. Anthony Blvd., N., 3101 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | - | Minfang Wu |  | Existing facility | Inspection to collect information or data about the facility This FSE has 2 grease traps one to the right of the 3 basin sink and one in the basement. There is also a single basin sink not connected to the grease trap that we have asked them to put a sig |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | PASS - Passed Inspection | Minfang Wu |  | Existing facility | A grease trap/interceptor inspection performed Grease trap in the basement that receives flow form the Wok stoves is in functional working order. |  | No
[4397] Chung King Express - 3101 N. Anthony Blvd. Anthony Blvd., N., 3101 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | PASS - Passed Inspection | Minfang Wu |  | Existing facility | A grease trap/interceptor inspection performed Grease trap that receives flow form the 3 Basin sink. This is a metal unit and was just starting to show some corrosion on the Effluent side. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | - | Minfang Wu |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-24 | MAR | 2026-02-24 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed FSE has 2 Grease traps, one after the 3 basin sink and one in the basement that catches all flow from the Wok |  | No
[4397] Chung King Express - 3101 N. Anthony Blvd. Anthony Blvd., N., 3101 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-24 | MAR | 2026-02-24 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection FSE has 2 sampling ports one for the Wok and one for the 3 basin sink |  | No
[9445] Circle K - 2304 Sherman Blvd. Sherman Blvd., 2304 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Mod Check | Monitoring point inspection functional/new condition with steps in place. Modification event can be closed |  | No
[18419] Clean Eatz - 4916 Illinois Rd. Ste 114 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-15 | COS | 2025-10-15 | COS | - | - |  |  | Existing Facility | Inspection to collect information or data about the facility Grease trap needs cleaned and they need to increase cleaning frequency to every 14 calendar days |  | No
[18419] Clean Eatz - 4916 Illinois Rd. Ste 114 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-15 | COS | 2025-10-15 | COS | - | - |  |  | Existing Facility | A grease trap/interceptor inspection performed Functional condition with all components in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-15 | COS | 2025-10-15 | COS | - | - |  |  | Existing Facility | Monitoring point inspection Sampling port in functional condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-15 | COS | 2025-10-15 | COS | - | - |  |  | Existing Facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[4227] CLOSED - 5701 Coldwater Rd. Coldwater Rd., 5701 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | DVS | A grease trap/interceptor inspection performed GI was in functional condition with the outlet tee/downleg in place as well as the center baffle. Walls and baffle in functional condition |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | DVS | Monitoring point inspection functional condition |  | No
[7276] CLOSED - 4515 Maplecrest Rd. Maplecrest Rd., 4515 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-17 | COS | 2025-09-17 | MAR | - | - |  | Noah Crouse | Sampling Viability | Inspection to collect information or data about the facility went to inspect and the facility has been closed. |  | No
[9985] CLOSED - 5925 N. Clinton St. Clinton St., N., 5925 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | Inspection to collect information or data about the facility Investigation from a degreasing line. They had a sign on the window stating that they are closed and a new bakery will be moving in. |  | No
[0948] Coliseum Donuts - 1530 N. Coliseum Blvd. Coliseum Blvd., N., 1530 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-09 | MAR | 2026-03-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease trap needs pumped, overly full |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-09 | MAR | 2026-03-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | Monitoring point inspection CMH is backed up and needs to be pumped and jetted |  | No
[0948] Coliseum Donuts - 1530 N. Coliseum Blvd. Coliseum Blvd., N., 1530 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-09 | MAR | 2026-03-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[7742] Cook Spring/The Summit - 1025 W. Rudisill Blvd. Rudisill Blvd., W., 1025 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-15 | MAR | 2025-09-15 | MAR | - | FUNC - Fully Functional |  |  | CMH Inspection | Monitoring point inspection Inspected CMH to verify if a sample could be taken. CMH has a depth of 63" with 2 steps and a 90 degree turn at the bottom. 40" to first step and 59" to 2nd step. |  | No
[8006] Cookie Cottage - 620 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 620 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Grease Interceptor influent side has an elbow and not a tee. The FSE may be required to replace the elbow at a later date if maintenance needs to be done on influent inlet. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[8006] Cookie Cottage - 620 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 620 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | - | Maureen Madden |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9605] Corner Pocket Pub - 3215 St. Joe Ctr. Rd. St. Joe Ctr. Rd., 3215 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-27 | MAR | 2025-10-27 | MAR | - | - | Karole Schnepp | Shannon Riley | Existing facility | Inspection to collect information or data about the facility |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-27 | MAR | 2025-10-27 | MAR | - | - | Karole Schnepp | Shannon Riley | Existing facility | A grease trap/interceptor inspection performed Grease trap was opened and needed cleaned. Could not inspect. FSE was informed to clean and have an IPS employee on site to verify Extractor condition. |  | No
[9605] Corner Pocket Pub - 3215 St. Joe Ctr. Rd. St. Joe Ctr. Rd., 3215 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-25 | COS | 2025-11-25 | COS | - | - |  |  | Follow-up | A grease trap/interceptor inspection performed inspected right after a pump out. All components are in place. This model has built in diffusers that look like the inner wall |  | No
[1208] Cracker Barrel Old Country Store #62 - 1609 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1609 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-17 | MAR | 2025-10-17 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed No outlet tee was in place when the GoPro was utilized to see the inside of the Grease Interceptor. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-17 | MAR | 2025-10-17 | MAR | - | FUNC - Fully Functional |  |  | Existing facility | Monitoring point inspection |  | No
[18449] Crispy Cones - 5129 Illinois Rd. Ste. 106 Illinois Rd., 5129 Ste 106 Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-07 | SJR | 2025-11-07 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | A dye trace to prove the monitoring point belongs to the facility Confirmed location of CMH shared by entire strip mall |  | No
[3027] Curly's Village Inn - 4205 Bluffton Rd. Bluffton Rd., 4205 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - | Jerome Karn |  | Existing facility | Inspection to collect information or data about the facility FSE has a 2 basin sink and a dishwasher. No grease trap or sampling port on site. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - | Jerome Karn |  | Existing Facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[3027] Curly's Village Inn - 4205 Bluffton Rd. Bluffton Rd., 4205 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection | David Tolliver |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection | David Tolliver |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | - | David Tolliver |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17714] Dairy Queen #45536 - 5115 E. Dupont Rd. Dupont Rd., E., 5115 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9160] Dash-In - 814 S. Calhoun St. Calhoun St., S., 814 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-12 | MAR | 2025-11-12 | MAR | - | PASS - Passed Inspection | Emily Underwood |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-12 | MAR | 2025-11-12 | MAR | - | - | Emily Underwood |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17801] Domino's - 1532 W. Cook Rd. Cook Rd., W., 1532 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[17801] Domino's - 1532 W. Cook Rd. Cook Rd., W., 1532 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18479] Domino's - 5905 Bluffton Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-24 | MAR | 2026-02-24 | MAR | - | PASS - Passed Inspection | Chris Mayhall |  | Existing facility - Remodel | A grease trap/interceptor inspection performed |  | No
[18479] Domino's - 5905 Bluffton Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-24 | MAR | 2026-02-24 | MAR | - | PASS - Passed Inspection | Chris Mayhall |  | Existing facility - Remodel | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-24 | MAR | 2026-02-24 | MAR | - | - | Chris Mayhall |  | Existing facility - Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17770] Domino's #2639 - 1020 E. Tillman Rd. Tillman Rd., E., 1020 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[17770] Domino's #2639 - 1020 E. Tillman Rd. Tillman Rd., E., 1020 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17615] Domino's #2672 - 1940 N. Coliseum Blvd. Coliseum Blvd., N., 1940 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | - |  |  | Existing facility | A grease trap/interceptor inspection performed Needs pumped in the next 30 days |  | No
[17615] Domino's #2672 - 1940 N. Coliseum Blvd. Coliseum Blvd., N., 1940 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9255] Don Chava's - 1234 N. Wells St. Wells St., N., 1234 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-04 | MAR | 2025-11-04 | MAR | - | PASS - Passed Inspection | Ricardo Roque Jr. |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[9255] Don Chava's - 1234 N. Wells St. Wells St., N., 1234 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-04 | MAR | 2025-11-04 | MAR | - | - | Ricardo Roque Jr. |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[3605] Don Hall's Prime Rib - 2005 E. State Blvd. State Blvd., E., 2005 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - | Anna Heath |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1237] Dos Margaritas - 4230 N. Clinton St. Clinton St., N., 4230 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Exceedance Investigation | Inspection to collect information or data about the facility Water heater set to 190, pumped every 3 months by 3 sons, recommended contacting hauler for information on previous pump outs. Recommended reviewing best management practices with staff. |  | No
[1237] Dos Margaritas - 4230 N. Clinton St. Clinton St., N., 4230 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Exceedance Investigation | A grease trap/interceptor inspection performed Flat top grease tray - dumped in grease hopper Flat top grease tray - dumped in grease hopper 2 Basin do not flow to interceptor 3 Basin and prewash are used for dishes 1 basin by 2 basin is used for h |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Exceedance Investigation | Monitoring point inspection Flat top grease tray - dumped in grease hopper 2 basin do not flow to intercepter 3 basin and prewash are all used for hand sink |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | COS | 2025-09-22 | COS | - | - |  |  | Exceedance Investigation | Outreach to a facility manager where an outreach binder is delivered & explained Recommended contacting hauler for information on previous pump outs. Recommended reviewing best management practices with staff. |  | No
[18465] Drive & Shine Car Wash - 1103 E. Coliseum Blvd. Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non-FSE | A dye trace to prove the monitoring point belongs to the facility confirmed the CMH |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non- FSE | A grease trap/interceptor inspection performed functional condition with inlet and outlet tee/downlegs in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non-FSE | Monitoring point inspection functional/new condition |  | No
[18473] Drive & Shine Car Wash - 4809 Illinois Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-23 | COS | 2025-12-23 | COS | - | - |  |  | New Build | Monitoring point inspection functional condition |  | No
| Inspection Oil/Sand Separator - An oil separator inspection performed |  |  | 2025-12-23 | COS | 2025-12-23 | COS | - | - |  |  | New Build | An oil separator inspection performed functional condition with inlet and outlet tee/downleg in place |  | No
[18467] Drive & Shine Lube Center - 1115 E. Coliseum Blvd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non-FSE | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator confirmed the floor drains flow to O/S |  | No
[18467] Drive & Shine Lube Center - 1115 E. Coliseum Blvd. Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non-FSE | A dye trace to prove the monitoring point belongs to the facility confirmed CMH |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non-FSE | A grease trap/interceptor inspection performed functional/new condition with inlet and outlet tee/downlegs |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-10 | COS | 2025-11-10 | COS | - | - |  | Noah Crouse | New Build - Non-FSE | Monitoring point inspection functional/new condition |  | No
[18474] Drive & Shine Lube Center - 4811 Illinois Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-23 | COS | 2025-12-23 | COS | - | - |  |  | New Build | Monitoring point inspection functional condition |  | No
| Inspection Oil/Sand Separator - An oil separator inspection performed |  |  | 2025-12-23 | COS | 2025-12-23 | COS | - | - |  |  | New Build | An oil separator inspection performed Inlet and outlet tee/downleg in place |  | No
[18471] Dunkin Donuts - 7607 S. Anthony Blvd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator confirmed that all kitchen fixtures flow to the interceptor |  | No
[18471] Dunkin Donuts - 7607 S. Anthony Blvd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  | Mark A Rekeweg | Remodel | Inspection to collect information or data about the facility the interceptor is a poly oil separator with 3 manholes. It is not concrete and the outlet tee is enclosed. The lids also say Oil Separator. We asked the Contractor for specs and are waiting fo |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  | Mark A Rekeweg | Remodel | A grease trap/interceptor inspection performed Functional/new condition. The interceptor is not to city spec. This is a poly oil separator being used as an interceptor. Facility has approval to use this since it is already installed. The outlet tee/downl |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  |  | Remodel | Monitoring point inspection functional condition |  | No
[10211] Dunkin Donuts #346590 - 8051 Coldwater Rd. Coldwater Rd., 8051 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-11-25 | COS | 2025-11-25 | COS | - | - |  |  | Pre-remodel and follow-up | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator 3-basin sink only flows to interceptor |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-25 | COS | 2025-11-25 | COS | - | - |  |  | Pre-remodel and follow-up | A dye trace to prove the monitoring point belongs to the facility confirmed that all drains except 3-basin flow to interceptor. They will need to correct this for the remodel |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-25 | COS | 2025-11-25 | COS | - | - |  |  | Pre-remodel and follow-up | Inspection to collect information or data about the facility All grease laden drains will need to be plumbed to the interceptor. The outlet manhole needs to have a manhole lid and casting installed. There needs to be an outlet tee/downleg installed if th |  | No
[10211] Dunkin Donuts #346590 - 8051 Coldwater Rd. Coldwater Rd., 8051 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-25 | COS | 2025-11-25 | COS | - | - |  |  | Pre-remodel and follow-up | A grease trap/interceptor inspection performed no evidence of corrosion. Cannot see outlet tee/downleg due to baffle. The outlet side is still not exposed. They will need to install an outlet manhole and casting. |  | No
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-03-12 | COS | 2026-03-12 | COS | - | - |  | Zachary Moorman | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator Old sewer line was plumbed to the interceptor. Restrooms were removed from this line and a new line was installed for them. |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2026-03-12 | COS | 2026-03-12 | COS | - | - |  | Zachary Moorman | Remodel | A dye trace to prove the monitoring point belongs to the facility New sanitary line for restrooms was traced to the CMH |  | No
[10211] Dunkin Donuts #346590 - 8051 Coldwater Rd. Coldwater Rd., 8051 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-12 | COS | 2026-03-12 | COS | - | - |  | Zachary Moorman | Remodel | A grease trap/interceptor inspection performed New risers and casting were installed on the outlet side of the interceptor. Outlet tee/downleg not installed |  | No
[0132] Eggster - In Cottage Flowers - 236 E. Wayne St. Wayne St., E., 236 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-20 | MAR | 2026-01-20 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | David Wall |  | Existing facility | A grease trap/interceptor inspection performed FSE was informed to clean grease trap and send photos |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-20 | MAR | 2026-01-20 | MAR | - | PASS - Passed Inspection | David Wall |  | Existing facility | Monitoring point inspection |  | No
[0132] Eggster - In Cottage Flowers - 236 E. Wayne St. Wayne St., E., 236 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-20 | MAR | 2026-01-20 | MAR | - | - | David Wall |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17819] El Taquero - 4507 Coldwater Rd., Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | PASS - Passed Inspection | Alberto Martinez |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | PASS - Passed Inspection | Alberto Martinez |  | Existing facility | Monitoring point inspection |  | No
[17819] El Taquero - 4507 Coldwater Rd., Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - | Alberto Martinez |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18455] Electric Works Phase II - Bldg A - 1450 Van Buren St. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-05 | COS | 2025-09-05 | COS | - | - |  | Mark A Rekeweg | Remodel | Inspection to collect information or data about the facility Control Manhole is offset and they were informed that they need to re-set the risers before concrete is poured |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-05 | COS | 2025-09-05 | COS | - | - |  | Mark A Rekeweg | Remodel | A grease trap/interceptor inspection performed Functional/new condition with outlet tee/downleg in place |  | No
[18455] Electric Works Phase II - Bldg A - 1450 Van Buren St. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-05 | COS | 2025-09-05 | COS | - | - |  | Mark A Rekeweg | Remodel | Monitoring point inspection functional condition 70 in deep no steps |  | No
[18480] Eleos Hospice Care - 6255 Topsfield Lane Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-23 | BSS | 2026-03-23 | BSS | - | PASS - Passed Inspection |  |  | New Build - DVS Control Manhole Inspection | Monitoring point inspection |  | No
[10000] Fairfield Inn and Suites - 6021 Lima Rd. Lima Rd., 6021 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-18 | MAR | 2025-09-18 | MAR | - | FUNC - Fully Functional |  |  | Verify depth of CMH | Monitoring point inspection CMH is 44" deep - 16" to first step - 32" to second step. Looks like the first step may be in the way of setting a sampler in the CMH. Rough measurement was 14-16 inches between the edge of the first step and the ring of the C |  | No
[6403] Fazoli's Restaurant #5908 - 439 W. Coliseum Blvd. Coliseum Blvd., W., 439 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-03 | MAR | 2026-02-03 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Jessica Miller |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is over full and FSE was unable to verify a center baffle |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-03 | MAR | 2026-02-03 | MAR | - | PASS - Passed Inspection | Jessica Miller |  | Existing facility | Monitoring point inspection |  | No
[6403] Fazoli's Restaurant #5908 - 439 W. Coliseum Blvd. Coliseum Blvd., W., 439 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-03 | MAR | 2026-02-03 | MAR | - | - | Jessica Miller |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Jessica Miller |  | Existing facility | A grease trap/interceptor inspection performed Still need Grease Interceptor pumped so we can see interior |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | PASS - Passed Inspection | Jessica Miller |  | Existing facility | Monitoring point inspection |  | No
[6403] Fazoli's Restaurant #5908 - 439 W. Coliseum Blvd. Coliseum Blvd., W., 439 Fort Wayne
| Informational - Inspection to collect information or data about the facility | Completed Late |  | 2026-03-31 | MAR | 2026-04-01 | MAR | - | - | Jessica Miller |  | Existing facility | Inspection to collect information or data about the facility FSE was informed that the grease interceptor did not have a center baffle. They will be put back on the sampling protocol. They were informed that if we see an issue in our testing or other sew |  | Yes
[6404] Fazoli's Restaurant #5909 - 6525 Stellhorn Rd. Stellhorn Rd., 6525 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed FSE was recommended to have grease trap pumped soon. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[6404] Fazoli's Restaurant #5909 - 6525 Stellhorn Rd. Stellhorn Rd., 6525 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18484] Five Guys Burgers and Fries - 4978 E. Dupont Rd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-27 | COS | 2026-03-27 | COS | - | - |  | Mark A Rekeweg | External structures | Inspection to collect information or data about the facility there is a separate contractor for the inside plumbing so it will be dye traced once that is complete |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-27 | COS | 2026-03-27 | COS | - | - |  | Mark A Rekeweg | External structures | A grease trap/interceptor inspection performed functional/new condition with center baffle and outlet tee/downleg in place |  | No
[18484] Five Guys Burgers and Fries - 4978 E. Dupont Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-27 | COS | 2026-03-27 | COS | - | - |  | Mark A Rekeweg | External Structures | Monitoring point inspection Functional/new condition |  | No
[18485] FWFC - Stadium - 6411 Bass Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-27 | COS | 2026-03-27 | COS | - | - |  | Mark A Rekeweg | New build | A grease trap/interceptor inspection performed all 4 in functional condition with center baffles and outlet tee/downlegs |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-27 | COS | 2026-03-27 | COS | - | - |  | Mark A Rekeweg | New build | Monitoring point inspection Functional/new condition with 1 step in place |  | No
[17627] GiGi's Playhouse - 6081 N. Clinton St. Clinton St., N., 6081 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | A grease trap/interceptor inspection performed functional condition with all components in place. The grease trap was over capacity and had been cleaned a month before. They said it gets cleaned every 6 months to a year. They were told to increase cleani |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17802] Giordano's - 10180 Diebold Rd. Diebold Rd., 10180 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor needs to be pumped and jetted. |  | No
[17802] Giordano's - 10180 Diebold Rd. Diebold Rd., 10180 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17407] Golden Corral - 5335 Distribution Dr. Distribution Dr., 5335 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor was over full. Unable to see the condition of the center baffle. |  | No
[17407] Golden Corral - 5335 Distribution Dr. Distribution Dr., 5335 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18101] Guadalupe's Georgetown - 6540 E. State Blvd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-16 | COS | 2025-09-16 | MAR | - | - |  |  | Sampling event | Monitoring point inspection could not open cleanout. This is not the first time so a letter will be sent to require that the cleanout is accessible for sampling |  | No
[17395] Hardees - 5918 Lima Rd. Lima Rd., 5918 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE was reminded that External Grease Interceptors are to be cleaned at a minimum of every 3 months. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[17395] Hardees - 5918 Lima Rd. Lima Rd., 5918 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18477] Harvest Fellowship Church - 1001 W. Wallen Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-02 | COS | 2026-01-02 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed functional/new condition with all components in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-02 | COS | 2026-01-02 | COS | - | - |  |  | Remodel | Monitoring point inspection sampling port is in functional/new condition control manhole is in functional condition |  | No
[18477] Harvest Fellowship Church - 1001 W. Wallen Rd. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-02 | COS | 2026-01-02 | COS | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9392] Headwaters Church - 2000 N. Wells St. Wells St., N., 2000 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-01-29 | COS | 2026-01-29 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator all fixtures in the kitchen flow to the grease interceptor except the dishwasher. Did not dye trace the concessions or the coffee bar |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2026-01-29 | COS | 2026-01-29 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to prove the monitoring point belongs to the facility dishwasher flows to the CMH |  | No
[9392] Headwaters Church - 2000 N. Wells St. Wells St., N., 2000 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-29 | COS | 2026-01-29 | COS | - | - |  | Mark A Rekeweg | Remodel | A grease trap/interceptor inspection performed center baffle and outlet tee/downleg are in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-29 | COS | 2026-01-29 | COS | - | - |  | Mark A Rekeweg | Remodel | Monitoring point inspection functional condition |  | No
[17892] Healthy Vibes - 9171 Lima Rd. Lima Rd., 9171 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | PASS - Passed Inspection | Brandy O'Reilly |  | Existing facility - Remodel | A grease trap/interceptor inspection performed |  | No
[17892] Healthy Vibes - 9171 Lima Rd. Lima Rd., 9171 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | PASS - Passed Inspection | Brandy O'Reilly |  | Existing facility - Remodel | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | - | Brandy O'Reilly |  | Existing facility - Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9678] Hi Ho Again - 3620 E. Yoder Rd. Yoder Rd., E., 3620 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Betsy Kleber |  | Existing facility | A grease trap/interceptor inspection performed Grease trap needs cleaned |  | No
[9678] Hi Ho Again - 3620 E. Yoder Rd. Yoder Rd., E., 3620 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | - | Betsy Kleber |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9498] Hook & Ladder - 2616 Lwr. Huntington Rd. Lwr. Huntington Rd., 2616 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-30 | MAR | 2025-10-30 | MAR | - | PASS - Passed Inspection | Jennifer Flores |  | Existing facility | Inspection to collect information or data about the facility FSE is a bar in Waynedale. It does not have a dishwasher. Only appliances are a Ninja air fryer and Ninja pizza oven. Pizza's are purchased frozen and air fryer is wiped clean not washed. |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-30 | MAR | 2025-10-30 | MAR | - | PASS - Passed Inspection | Jennifer Flores | Shannon Riley | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[6418] Hopsing Chinese Food - 6214 Stellhorn Rd. Stellhorn Rd., 6214 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-19 | MAR | 2025-11-19 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Gui Jin Jiang |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor needs cleaned and jetted |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-19 | MAR | 2025-11-19 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Gui Jin Jiang |  | Existing facility | Monitoring point inspection CMH needs cleaned and jetted |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-28 | COS | 2026-01-28 | COS | - | - |  | Noah Crouse | Sampling Investigation | Monitoring point inspection manhole backed up. Nobody present to inform. |  | No
[6418] Hopsing Chinese Food - 6214 Stellhorn Rd. Stellhorn Rd., 6214 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-10 | MAR | 2026-02-10 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is over the baffle |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-10 | MAR | 2026-02-10 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | Monitoring point inspection |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Inspection to collect information or data about the facility Inspection to verify that CMH is cleaned and that the Grease Interceptor was pumped. |  | No
[6418] Hopsing Chinese Food - 6214 Stellhorn Rd. Stellhorn Rd., 6214 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[18463] Hoshi Hoshi - 5129 Illinois Rd. Ste. 108 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-28 | SJR | 2025-10-28 | SJR | - | - |  | Mark A Rekeweg |  | Inspection to collect information or data about the facility Indoor GT under 3 basin sink. No CMH/sampling port located and will be required to install within 120 days. |  | No
[18463] Hoshi Hoshi - 5129 Illinois Rd. Ste. 108 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-28 | SJR | 2025-10-28 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | A grease trap/interceptor inspection performed Grease trap was full and lots of build up and mold. Under new owners (approximately 2 months) and they had not cleaned GT. Cleaning is required so that it can be fully inspected. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-28 | SJR | 2025-10-28 | SJR | - | - |  | Mark A Rekeweg |  | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-07 | SJR | 2025-11-07 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | A dye trace to prove the monitoring point belongs to the facility Confirmed location of CMH shared by entire strip mall |  | No
[17458] Hungry Howie's Pizza - 4214 Cresent Ave. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Shared with all tenants of the strip |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection Shared with all tenants of the strip |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0051] Iceway Express - 3996 Ice Way Ice Way, 3996 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Sampling Viability | A grease trap/interceptor inspection performed grease interceptor was full and grease was hardened. There was grease inside the outlet tee which means grease is leaving the grease interceptor. The outlet tee/downleg was in place, but no inlet tee. Could |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Sampling Viability | Monitoring point inspection Functional condition with some grease buildup along the channel |  | No
[18085] Icing for Izaac - 243 Airport North Office Park Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-05 | COS | 2025-09-05 | COS | - | - |  |  | Compliance Inspection | Inspection to collect information or data about the facility inspected due to past exceedances and their requirement to come into compliance. They installed a new grease trap. They also had removed a stack of unscraped dishes from the sink. Their fine h |  | No
[18085] Icing for Izaac - 243 Airport North Office Park Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-05 | COS | 2025-09-05 | COS | - | - |  |  | Compliance Inspection | Monitoring point inspection Evidence of grease buildup |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-10 | COS | 2025-09-10 | COS | - | - |  |  | Compliance Inspection | A grease trap/interceptor inspection performed Installed 8/25/25, FOG is 1-2" thick than fluffy FOG New grease trap is 25 gpm and has all internal components in place |  | No
[18085] Icing for Izaac - 243 Airport North Office Park Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-31 | COS | 2026-03-31 | COS | - | - |  | Jeffrey Osborne | Fine Suspension investigation sample | Inspection to collect information or data about the facility sample was taken as part of the fine suspension compliance plan. This was the 2nd sample so if this one passes, they will not have to repay the original fine. The owner called the shop whil |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-31 | COS | 2026-03-31 | COS | - | - |  | Mark A Rekeweg | Fine Suspension investigation Sample | A grease trap/interceptor inspection performed Jeff Osborne, Manager of Operations was also Present functional condition. 4+" of fluffy FOG in the top. Overdue for cleaning. Owner stated last cleaning was 3/20/26 |  | No
[18466] Iggy's Subs - 6423 Lima Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-07 | COS | 2025-11-07 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed functional condition with all components in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-07 | COS | 2025-11-07 | COS | - | - |  |  | DVS Request | Monitoring point inspection Functional condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-07 | COS | 2025-11-07 | COS | - | - |  |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[7700] IHOP #5465 (CUGC) - 1535 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1535 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | - | Margy Hooker |  | Existing facility | Inspection to collect information or data about the facility FSE has inquired about the Grease Coop. |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Margy Hooker |  | Existing facility | A grease trap/interceptor inspection performed Unable to see center baffle due to over full Grease Interceptor. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | PASS - Passed Inspection | Margy Hooker |  | Existing facility | Monitoring point inspection |  | No
[7700] IHOP #5465 (CUGC) - 1535 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1535 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | - | Margy Hooker |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-21 | COS | 2026-01-21 | COS | - | - |  |  | Maint. Check | A grease trap/interceptor inspection performed grease interceptor was pumped and pressure washed during inspection. Interceptor is in functional condition |  | No
[9292] Indiana Mexican Bakery - 1419 N. Wells St. Wells St., N., 1419 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-04 | MAR | 2025-11-04 | MAR | - | PASS - Passed Inspection | German Pontoja |  | Existing facility | A grease trap/interceptor inspection performed Extractor is functional |  | No
[9292] Indiana Mexican Bakery - 1419 N. Wells St. Wells St., N., 1419 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-04 | MAR | 2025-11-04 | MAR | - | - | German Pontoja |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17390] Jalapenos Mexican Grill III - 6121 N Clinton St Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | Inspection to collect information or data about the facility 3-basin sink in the dish area is plumbed with dishwasher and bypasses the grease trap. They were told to connect the 3-basin sink in the dish area to the grease trap under the pre-wash sink |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | A grease trap/interceptor inspection performed both grease traps are in functional condition with all components in place. Both grease traps are cleaned every week |  | No
[17390] Jalapenos Mexican Grill III - 6121 N Clinton St Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17357] Jimmy John's - 4226 Crescent Ave Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Shared with all tenants of the strip |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection Shared with all tenants of the strip |  | No
[17357] Jimmy John's - 4226 Crescent Ave Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-12 | MAR | 2026-02-12 | COS | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9002] Jimmy Johns Gourmet Sandwiches - 101 W. Wayne St. Wayne St., W., 101 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-12 | MAR | 2025-11-12 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Stanita Shores |  | Existing facility | A grease trap/interceptor inspection performed Grease trap rusted out |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-12 | MAR | 2025-11-12 | MAR | - | - | Stanita Shores |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9892] Jimmy John's No. 982 - 5412 Coldwater Rd. Coldwater Rd., 5412 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor needs pumped and the FSE also has an outstanding 120 day letter to replace the grease interceptor. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9089] Kim Vu Vietnamese Cuisine - 433 E. Dupont Rd. Dupont Rd., E., 433 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed FSE owner said grease trap was cleaned weekly |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH is shared by whole strip mall |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9050] Koto Japanese Steakhouse & Sushi - 301 E. Washington Ctr. Rd. Washington Ctr. Rd., E., 301 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-10 | COS | 2025-09-10 | COS | - | - |  |  |  | A grease trap/interceptor inspection performed GI was pumped recently and not entirely full. Verified outlet tee/downleg |  | No
[9169] Kyaw Family Convenience Store LLC - 900 E. Pettit Ave. Pettit Ave., E., 900 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | DVS Request | Inspection to collect information or data about the facility Information from the email to DVS: I went and spoke with the owner today. I gathered some information below: -They removed the 3-basin and grease trap from the facility at 900 E. Pettit A |  | No
[18486] La Cabana 2 - 6209 E. State Blvd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-31 | MAR | 2026-03-31 | MAR | - | - | Adrian Lara | Carleen Sanzone | DVS Request | Inspection to collect information or data about the facility DVS needs to review documentation and potential variance. Dishwasher and pre wash currently bypass the sampling port and grease trap. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-31 | MAR | 2026-03-31 | MAR | - | - | Adrian Lara |  | DVS Request | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-31 | MAR | 2026-03-31 | MAR | - | PASS - Passed Inspection | Adrian Lara |  | DVS Request | Monitoring point inspection |  | No
[18486] La Cabana 2 - 6209 E. State Blvd. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-31 | MAR | 2026-03-31 | MAR | - | - | Adrian Lara |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1135] La Michoacana Ice Cream - 1903 W. Coliseum Blvd. Coliseum Blvd., W., 1903 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Recommend grease interceptor be pumped Outdoor grease interceptors are to be pumped at a minimum of every 3 months |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[1135] La Michoacana Ice Cream - 1903 W. Coliseum Blvd. Coliseum Blvd., W., 1903 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[2346] La Santa Anita Family Grill - 3310 Lafayette St. Lafayette St., 3310 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-08 | MAR | 2025-12-08 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[2346] La Santa Anita Family Grill - 3310 Lafayette St. Lafayette St., 3310 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-08 | MAR | 2025-12-08 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0231] Lassus Handy Dandy - 3610 E. Dupont Rd. Dupont Rd., E., 3610 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-20 | MAR | 2025-10-20 | MAR | - | NO_OBSRV - Could not Observe |  |  | Existing facility | A grease trap/interceptor inspection performed Could not see center baffle will need to inspect during pump out |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-20 | MAR | 2025-10-20 | MAR | - | FUNC - Fully Functional |  |  | Existing facility | Monitoring point inspection |  | No
[0231] Lassus Handy Dandy - 3610 E. Dupont Rd. Dupont Rd., E., 3610 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-20 | MAR | 2025-10-20 | MAR | - | FUNC - Fully Functional |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-11 | MAR | 2025-12-11 | MAR | - | - | Maya Cunningham |  | Existing facility | A grease trap/interceptor inspection performed Went to verify center baffle but was unable to see such baffle |  | No
[0034] Lassus Handy Dandy #41 - 10040 Lima Rd. Lima Rd., 10040 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | Maint check | Monitoring point inspection manhole appears to have been jetted. There is no longer toilet paper all over the manhole bottom and there were pressure washer marks on the risers. There was still sanitary in the line but it just appears that the customers u |  | No
[0034] Lassus Handy Dandy #41 - 10040 Lima Rd. Lima Rd., 10040 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | Monitoring point inspection Backed up with sanitary |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10237] Lassus Handy Dandy #46 - 8830 Coldwater Rd. Coldwater Rd., 8830 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-21 | MAR | 2025-10-21 | MAR | - | - |  |  | Existing Facility | Inspection to collect information or data about the facility Grease Interceptor needs cleaned so we can see the interior components. Yellow dye was used to verify the CMH that is in then corner by the Car Wash. |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-21 | MAR | 2025-10-21 | MAR/NSC | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing Facility | A grease trap/interceptor inspection performed Unable to inspect Grease Interceptor. Will need to return when pumped so we can see all components |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-21 | MAR | 2025-10-21 | MAR/NSC | - | FUNC - Fully Functional |  |  | Existing Facility | Monitoring point inspection |  | No
[9610] Latch String Bar and Grill - 3221 N. Clinton St. Clinton St., N., 3221 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-06 | MAR | 2025-11-06 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE did not have a grease trap or sampling port. A hand sink, mop sink and 3 basin sink are there. Fry oil and grease go out into a grease hopper. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-06 | MAR | 2025-11-06 | MAR | - | - | Mike Bentz |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[456] Lee's Famous Recipe Chicken #207551(CUGC) - 6316 Stellhorn Rd. Stellhorn Rd., 6316 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-30 | COS | 2025-12-30 | MAR | - | - |  | Jeffrey Osborne | Sample Investigation | Monitoring point inspection Control manhole was backed up during a sampling event so facility was told to pump and jet within 30 days. Jeff came out and verified the control manhole was backed up |  | No
[3919] Lexy's Pizza - 908 Spring St. Spring St., 908 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE needs to have licensed plumber install a grease trap after the 3 Basin sink and a sampling port after the Grease trap. Employee was did not feel comfortable signing the Inspection report. I |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18461] Life in Balance Nutrition - 208 E Pettit Ave. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-30 | SJR | 2025-10-30 | SJR | - | - |  |  | Existing Facility | Inspection to collect information or data about the facility No grease trap or CMH/sampling port located at facility. Facility did have a 3 basin sink. |  | No
[18461] Life in Balance Nutrition - 208 E Pettit Ave. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-30 | SJR | 2025-10-30 | SJR | - | - |  | Mark A Rekeweg |  | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-20 | MAR | 2026-02-20 | MAR | - | PASS - Passed Inspection | Marcos Zepeda |  | Existing facility | A grease trap/interceptor inspection performed Grease trap was installed on 2.19.26 |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-20 | MAR | 2026-02-20 | MAR | - | PASS - Passed Inspection | Marcos Zepeda |  | Existing facility | Monitoring point inspection Sampling port was installed 2.19.26 |  | No
[18475] Lighthouse Coffee Bar in DO McComb & Sons - 1320 E. Dupont Rd Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed functional condition with all components in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | Remodel | Monitoring point inspection functional condition. This was a variance approved to allow a cleanout |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9032] Little Caesar's #1338-20 - 211 E. Rudisill Blvd. Rudisill Blvd., E., 211 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-30 | MAR | 2026-03-30 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Grease trap should be pumped and cleaned every 2 weeks according to City rules and regulations |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-30 | MAR | 2026-03-30 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9930] Little Caesar's #1338-22 - 5722 Maplecrest Rd. Maplecrest Rd., 5722 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | PASS - Passed Inspection | Aaron Paholak |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[9930] Little Caesar's #1338-22 - 5722 Maplecrest Rd. Maplecrest Rd., 5722 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-20 | MAR | 2025-11-20 | MAR | - | - | Aaron Paholak |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17498] Little Caesar's #1338-27 - 6302 Illinois Rd. Illinois Rd., 6302 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[17498] Little Caesar's #1338-27 - 6302 Illinois Rd. Illinois Rd., 6302 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[8150] Logan's Roadhouse - 1210 Illinois Rd. Illinois Rd., 1210 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-01-15 | COS | 2026-01-15 | COS | - | - |  |  | DVS Request | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator facility informed us that they replumbed the DW. They had replumbed it to the pre-wash sink. There doesn’t seem to be any close sanitary drain |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-15 | COS | 2026-01-15 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed functional condition - excess grease buildup even after jetting. Hoping the grease will soften over time |  | No
[10195] Loving Café - 7605 Coldwater Rd. Ste. A Coldwater Rd., 7605 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-17 | MAR | 2025-11-17 | MAR | - | PASS - Passed Inspection | George Le |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-17 | MAR | 2025-11-17 | MAR | - | - | George Le |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10234] Lunchbox Café II Inc. - 8814 Coldwater Rd. Coldwater Rd., 8814 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-12 | COS | 2025-09-12 | COS | - | - |  |  | Sampling viability | Monitoring point inspection CMH previously listed as a sampling port. Went and verified that it is a capped cleanout and is not eligible for sampling |  | No
[17320] Magadoo Asian Grocery - 5945 N. Clinton St. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-30 | COS | 2026-01-30 | COS | - | - |  | Mark A Rekeweg | Investigation | Inspection to collect information or data about the facility Inspected to see if there was any change in process. They do not package, prep, or wash anything in the facility. |  | No
[6546] Mama Mia Pizza - 6656 St. Joe Rd. Ste. A St. Joe Rd., 6656 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-27 | MAR | 2025-10-27 | MAR | - | - | Todd Blanton | Shannon Riley | Existing facility | Inspection to collect information or data about the facility FSE was inspected for Grease trap and Sampling Port. Grease trap is functional but Sampling Port is missing. FSE was informed to contact a licensed plumber to have Sampling port installed. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-27 | MAR | 2025-10-27 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Todd Blanton | Shannon Riley | Existing facility | A grease trap/interceptor inspection performed Grease had not been cleaned. FSE was informed to clean and contact IPS to come and re inspect. |  | No
[6546] Mama Mia Pizza - 6656 St. Joe Rd. Ste. A St. Joe Rd., 6656 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-28 | MAR | 2025-10-28 | MAR | - | FUNC - Fully Functional | Todd Blanton | Shannon Riley | Existing Facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-29 | MAR | 2025-10-29 | MAR | - | PASS - Passed Inspection | Todd Blanton |  | Existing facility | Inspection to collect information or data about the facility Inspected Grease trap. Trap passed |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-29 | MAR | 2025-10-29 | MAR/NSC | - | PASS - Passed Inspection | Todd Blanton |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[18483] Marathon gas station (east tenant space) - 4619 Bass Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New Build | A grease trap/interceptor inspection performed functional condition with center baffle in place. Outlet tee/downleg missing Picture sent with new outlet tee/downleg installed 3.20.26 |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New build | Monitoring point inspection Functional/New condition |  | No
[18482] Marathon gas station (west tenant space) - 4619 Bass Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New Build | A grease trap/interceptor inspection performed functional condition with center baffle in place. Outlet tee/downleg missing Picture sent with new outlet tee/downleg installed 3.20.26 |  | No
[18482] Marathon gas station (west tenant space) - 4619 Bass Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New Build | Monitoring point inspection Functional/new condition |  | No
[6263] Marco's Pizza #1055 - 1612 St. Joe Ctr. Rd. St. Joe Ctr. Rd., 1612 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-28 | COS | 2025-10-28 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed Functional condition with all components in place |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-28 | COS | 2025-10-28 | COS | - | - |  |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18434] MB - Brown Bears Kitchen - 1219 Rivermet Ave. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | MAR | 2025-09-22 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New FT | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18433] MB - Cocina 787 - 10835 Smokey Ridge Pl. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | MAR | 2025-09-22 | COS | - | FUNC - Fully Functional |  |  | DVS Request - New FT | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18435] MB - Enjoy God's Glory - 609 Oak St. New Haven
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | MAR | 2025-09-22 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New FT | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18432] MB - Epic Eats LLC - 304 E. 700 N Huntington
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | MAR | 2025-09-22 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New Food truck | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18438] MB - Frowniez LLC - 548 Montclair Dr. New Haven
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-23 | MAR | 2025-09-23 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New Food truck | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18439] MB - Hot Dog Boyz LLC - 4014 South Park Dr. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained | Completed Late |  | 2025-10-01 | MAR | 2025-10-02 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New Food truck | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18437] MB - Hya Caribbean Cuisine - 3828 E. State Blvd. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-23 | MAR | 2025-09-23 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New Vendor | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18436] MB - Nomad Coffee - 2620 Jacobs Creek Run Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | MAR | 2025-09-22 | MAR | - | FUNC - Fully Functional |  |  | DVS Request - New Food Cart | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18426] MB - The Flavor Stable - 1024 Aylesford Dr. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-22 | MAR | 2025-09-22 | MAR | - | FUNC - Fully Functional |  |  | DVS Request New Mobile FSE | Outreach to a facility manager where an outreach binder is delivered & explained |  | Yes
[18472] McAlister's Deli - 5552 Meijer Dr. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  |  | New Build | A grease trap/interceptor inspection performed functional/new condition. There is no outlet tee, but they will send photos once it gets installed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  |  | New Build | Monitoring point inspection functional/new condition |  | No
[8205] McAlister's Deli #100966 - 6709 Lima Rd. Lima Rd., 6709 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Grease Interceptor was pumped by Gleason Sanitation. |  | Yes
[8205] McAlister's Deli #100966 - 6709 Lima Rd. Lima Rd., 6709 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor was inspected and is functional |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | - | Lisa Cain |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[847] McDonald's #4792 - 1333 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1333 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-17 | MAR | 2025-10-17 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Was unable to verify a downleg in the grease Interceptor. FSE was informed to pump and jet the G/I and that we would return to inspect in 30 days. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-17 | MAR | 2025-10-17 | MAR | - | FUNC - Fully Functional |  |  | Existing facility | Monitoring point inspection |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-11 | MAR | 2025-12-11 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[6146] McDonald's #4958 - 1103 Goshen Rd. Goshen Rd., 1103 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-27 | MAR | 2026-02-27 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18458] Mi Tierra Market - 122 E. Rudisill Blvd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-10-01 | COS | 2025-10-01 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator all kitchen fixture to GT |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-10-01 | COS | 2025-10-01 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to prove the monitoring point belongs to the facility effluent of GT |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-01 | COS | 2025-10-01 | COS | - | - |  | Mark A Rekeweg | Remodel | A grease trap/interceptor inspection performed functional/new condition. Outlet tee/downleg and center baffle in place |  | No
[18458] Mi Tierra Market - 122 E. Rudisill Blvd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-01 | COS | 2025-10-01 | COS | - | - |  | Mark A Rekeweg | Remodel | Monitoring point inspection Functional/new condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-01 | COS | 2025-10-01 | COS | - | - |  | Mark A Rekeweg | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17557] Miss Beth's Coffee - 2339 Crescent Ave. Crescent Ave., 2339 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-05 | COS | 2026-03-05 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed Functional condition. The screen around the outlet downleg was not in properly. I also had concerns because the grease trap has previously been fabricated and it is flimsy. I recommended that they replace th |  | No
[17557] Miss Beth's Coffee - 2339 Crescent Ave. Crescent Ave., 2339 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-05 | COS | 2026-03-05 | COS | - | - |  |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17359] Miss J's Diner - 3039 Goshen Rd. Goshen Rd., 3039 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-06 | COS | 2025-10-06 | COS | - | - |  |  | CMH inspect | Monitoring point inspection Went to see if the Manhole listed in the facility's info was actually a CMH. I believe it is a shared manhole |  | No
[9376] Mozzarelli's Pizza - 1820 W. Dupont Rd. Ste. A Dupont Rd., W., 1820 Ste. A Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Could not locate CMH due to snow cover. FSE owner claims manhole is north of the building in the field. |  | Yes
[9376] Mozzarelli's Pizza - 1820 W. Dupont Rd. Ste. A Dupont Rd., W., 1820 Ste. A Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease needs cleaning |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18468] Multi-tenant facility - 6008 Lima Rd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-19 | COS | 2025-11-19 | COS | - | - |  |  | New Build | Inspection to collect information or data about the facility facility will need sanitary manholes on all CMHs and to install outlet downlegs |  | No
[18468] Multi-tenant facility - 6008 Lima Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-19 | COS | 2025-11-19 | COS | - | - |  |  | New build | A grease trap/interceptor inspection performed functional condition. Outlet tee in place, but no down-leg |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-19 | COS | 2025-11-19 | COS | - | - |  |  | New Build | Monitoring point inspection all functional condition. They all had storm drain manhole, which they will need to swap with sanitary manholes lids before signoffs |  | No
[18476] Mystic Arcade - 4224 Coldwater Rd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-02 | MAR | 2026-01-02 | MAR | - | - |  |  | DVS Remodel | Inspection to collect information or data about the facility FSE is a remodel from a furniture store to an arcade. The FSE has a soda machine and will likely only sell popcorn other than pre packaged goods. Pop machine will need to be plumbed into he gre |  | Yes
[18476] Mystic Arcade - 4224 Coldwater Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-02 | MAR | 2026-01-02 | MAR | - | PASS - Passed Inspection |  |  | DVS Remodel | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-02 | MAR | 2026-01-02 | MAR | - | - |  |  | DVS Remodel | Monitoring point inspection Sampling port has been installed after the 3 Basin sink |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-02 | MAR | 2026-01-02 | MAR | - | - |  |  | DVS remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[2626] Nacho's Taqueria - 3739 S. Clinton St. Clinton St., S., 3739 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | - |  |  | Existing facility (Remodel) | Inspection to collect information or data about the facility * FSE has a single basin sink that is not connected to the grease trap. This sink is to be used for vegetable prep only and a sign should be placed above it stating that. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | PASS - Passed Inspection |  |  | Existing facility (Remodel) | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | PASS - Passed Inspection |  |  | Existing facility (Remodel) | Monitoring point inspection |  | No
[2626] Nacho's Taqueria - 3739 S. Clinton St. Clinton St., S., 3739 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | - |  |  | Existing facility (Remodel) | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0965] Noodles & Company - 4602 Illinois Rd Illinois Rd, 4602 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection Shared CMH |  | No
[0965] Noodles & Company - 4602 Illinois Rd Illinois Rd, 4602 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17373] Northeast Indiana Innovation Center - 3201 Stellhorn Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-13 | MAR | 2025-10-13 | MAR | - | FUNC - Fully Functional |  |  | Grease Interceptor inspection | A grease trap/interceptor inspection performed Grease Interceptors are in the breezeway in between the 2 buildings |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-13 | MAR | 2025-10-13 | MAR | - | FUNC - Fully Functional |  |  | CMH Inspection | Monitoring point inspection CMH is the western manhole when looking north. Very deep with many rungs. |  | No
[1476] Olive Garden #1186 - 315 W. Coliseum Blvd. Coliseum Blvd., W., 315 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  |  | A grease trap/interceptor inspection performed Needs cleaned and pumped and jetted |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1476] Olive Garden #1186 - 315 W. Coliseum Blvd. Coliseum Blvd., W., 315 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed unable to verify interior condition of Grease Interceptor |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH is working properly but needs cleaned there is a buildup of grease in the trench |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2026-04-14 | MAR | 2026-04-14 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE was informed that the center baffle and sides of the grease interceptor are showing deterioration. If further deterioration happens they may need to be replaced or restored to original cond |  | No
[1476] Olive Garden #1186 - 315 W. Coliseum Blvd. Coliseum Blvd., W., 315 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-14 | MAR | 2026-04-14 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor was pumped and cleaned on 4/14/26. It failed the inspection due to the outlet tee not being attached on the effluent pipe. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-14 | MAR | 2026-04-14 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH was jetted and cleaned on 4/14/26 |  | No
[17644] P. F. Changs - 4201 Coldwater Rd., Ste. D Coldwater Rd., 4201., Ste. D Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection | Shannon Smoker |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[17644] P. F. Changs - 4201 Coldwater Rd., Ste. D Coldwater Rd., 4201., Ste. D Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection | Shannon Smoker |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | - | Shannon Smoker |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18253] Pacos Buffet - 1531 Goshen Rd. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed functional/new condition with all components in place. The in-floor grease trap has been retired |  | No
[18253] Pacos Buffet - 1531 Goshen Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-10 | COS | 2025-12-10 | COS | - | - |  |  | DVS Request | Monitoring point inspection sampling port is in functional/new condition |  | No
[0134] Panda Express #1918 - 1414 Apple Glen Blvd. Apple Glen Blvd., 1414 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[0134] Panda Express #1918 - 1414 Apple Glen Blvd. Apple Glen Blvd., 1414 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17713] Papa John's #5012 - 5119 E. Dupont Rd. Dupont Rd., E., 5119 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Unable to see in the Grease Interceptor. FSE was informed to pump out Grease Interceptor and leave bolts out |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[17713] Papa John's #5012 - 5119 E. Dupont Rd. Dupont Rd., E., 5119 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-17 | MAR | 2026-02-17 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2026-04-16 | MAR | 2026-04-16 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE was informed to have the bolts removed from the Grease Interceptor. When I went to inspect they were still on. |  | No
[17732] Papi's Pizza - 224 E. Wallace St. 220 E. Wallace St. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-11 | COS | 2025-12-11 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed Functional condition. The inlet diffuser is missing and will need installed |  | No
[17732] Papi's Pizza - 224 E. Wallace St. 220 E. Wallace St. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-11 | COS | 2025-12-11 | COS | - | - |  |  | DVS Request | Monitoring point inspection functional condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-11 | COS | 2025-12-11 | COS | - | - |  |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0967] Phil's One Stop #13 - 2607 Goshen Rd Goshen Rd, 2607 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Sampling Viability | A grease trap/interceptor inspection performed grease interceptor is extremely full and needs pumped. The outlet tee was there and there was evidence of grease leaving the interceptor |  | No
[0967] Phil's One Stop #13 - 2607 Goshen Rd Goshen Rd, 2607 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Sampling Viability | Monitoring point inspection functional condition with evidence of grease along the channel |  | No
[4643] Pizza Hut Wingstreet - 6039 Stellhorn Rd. Stellhorn Rd., 6039 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-10 | MAR | 2026-02-10 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is overly full |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-10 | MAR | 2026-02-10 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[4643] Pizza Hut Wingstreet - 6039 Stellhorn Rd. Stellhorn Rd., 6039 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-10 | MAR | 2026-02-10 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-18 | COS | 2026-03-18 | COS | - | - |  |  | pumpout inspection | A grease trap/interceptor inspection performed functional condition with center baffle and outlet tee in place they did have grease build up inside the interceptor. They plan to jet during one of the next pumpouts. |  | No
[4642] Pizza Hut Wingstreet #6268 - 5801 St. Joe Rd. St. Joe Rd., 5801 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | - | Leanne Howk |  | Existing facility | Inspection to collect information or data about the facility FSE was inspected and the MH is 42" deep without steps. And it has a 2 manhole Grease Interceptor. |  | Yes
[4642] Pizza Hut Wingstreet #6268 - 5801 St. Joe Rd. St. Joe Rd., 5801 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | PASS - Passed Inspection | Leanne Howk |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is a 2 manhole model |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | - | Leanne Howk |  | Existing facility | Monitoring point inspection CMH is 42" deep with no steps |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | - | Leanne Howk |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[5796] Pizza King - 4226 Bluffton Rd. Bluffton Rd., 4226 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-15 | COS | 2025-10-15 | COS | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Facility does not have a grease trap or sampling location. They have been notified that w/in 120 days they must install a grease trap at the 3-basin and pre-wash and a sampling port |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-15 | COS | 2025-10-15 | COS | - | - |  |  | Existing Facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-30 | MAR | 2026-03-30 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[5796] Pizza King - 4226 Bluffton Rd. Bluffton Rd., 4226 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-30 | MAR | 2026-03-30 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[2612] Popeye's Chicken and Biscuits - 2615 S. Clinton St. Clinton St., S., 2615 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-05 | MAR | 2026-03-05 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-05 | MAR | 2026-03-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[2612] Popeye's Chicken and Biscuits - 2615 S. Clinton St. Clinton St., S., 2615 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-05 | MAR | 2026-03-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17777] Popeye's Louisiana Kitchen - 6111 Lima Rd. Lima Rd., 6111 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Sampling viability | A grease trap/interceptor inspection performed grease trap is completely full and needs pumped. There is evidence of grease leaving the interceptor |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-15 | COS | 2025-09-15 | COS | - | - |  |  | Sampling viability | Monitoring point inspection manhole directly after the grease trap cannot be used for sampling. It was not marked well so looking at the blueprints there is another manhole that I will need to go back out and inspect |  | No
[17760] Portillo's #63 - 295 W. Coliseum Blvd. Coliseum Blvd., W., 295 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | PASS - Passed Inspection | Gary Lyons |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | Monitoring point inspection CMH was backed up. FSE was informed to have CMH and grease interceptor pumped before it backed up into the facility. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-16 | MAR | 2025-12-16 | MAR | - | - | Gary Lyons |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17760] Portillo's #63 - 295 W. Coliseum Blvd. Coliseum Blvd., W., 295 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | PASS - Passed Inspection | Tony Hiatt |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Tony Hiatt |  | Existing facility | Monitoring point inspection A grease trap/interceptor inspection performed An excessive amount of sanitary waste was blocking the cmh trench |  | No
[1227] Rally's #9067 - 4810 Coldwater Rd. Coldwater Rd., 4810 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is over full and not working properly |  | No
[1227] Rally's #9067 - 4810 Coldwater Rd. Coldwater Rd., 4810 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | - |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[1227] Rally's #9067 - 4810 Coldwater Rd. Coldwater Rd., 4810 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
[1326] Rally's #9098 - 320 W. Jefferson Blvd. Jefferson Blvd., W., 320 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor needs to be pumped and cleaned |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[1326] Rally's #9098 - 320 W. Jefferson Blvd. Jefferson Blvd., W., 320 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9912] Rally's #9781 - 5607 S. Anthony Blvd. Anthony Blvd., S., 5607 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | - |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | Monitoring point inspection CMH could not be accessed due to overgrowth of landscaping. FSE was informed top have landscaping cut back so access to CMH is available |  | No
[9912] Rally's #9781 - 5607 S. Anthony Blvd. Anthony Blvd., S., 5607 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-30 | MAR | 2026-03-30 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-30 | MAR | 2026-03-30 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection Had to trim back considerable amount of landscaping to access the CMH |  | No
[4881] Red Lobster - 4825 Coldwater Rd. Coldwater Rd., 4825 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[6606] Renaissance Restaurant - 1033 E. Tillman Rd. Tillman Rd., E., 1033 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[0067] Rise N Roll Bakery & Deli - 5129 Illinois Rd. Ste. 101 Illinois Rd., 5129, Ste. 101 Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-07 | SJR | 2025-11-07 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | A dye trace to prove the monitoring point belongs to the facility Confirmed location of CMH shared by entire strip mall |  | No
[6409] Sabor y Sazon Colombiano/Encanto Latino Event Center - 2242 Goshen Rd. Goshen Rd., 2242 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | PASS - Passed Inspection | Jhou Rincon |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | PASS - Passed Inspection | Jhou Rincon |  | Existing facility | Monitoring point inspection |  | No
[6409] Sabor y Sazon Colombiano/Encanto Latino Event Center - 2242 Goshen Rd. Goshen Rd., 2242 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-11 | MAR | 2026-03-11 | MAR | - | - | Jhou Rincon |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained Explained Outreach packet to Jhou Rincon |  | No
[10131] Sam's Club #6313 - 6736 Lima Rd. Lima Rd., 6736 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-03 | MAR | 2025-12-03 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Inspected the Grease Interceptor and verified the CMH for Sam's Club. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-03 | MAR | 2025-12-03 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[10131] Sam's Club #6313 - 6736 Lima Rd. Lima Rd., 6736 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-03 | MAR | 2025-12-03 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-03 | MAR | 2025-12-03 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17574] Savvy Sliders - 7777 Coldwater Rd. Coldwater Rd., 7777 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-14 | COS | 2026-01-14 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed functional condition with all components in place |  | No
[17574] Savvy Sliders - 7777 Coldwater Rd. Coldwater Rd., 7777 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-14 | COS | 2026-01-14 | COS | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9775] Sbarro - 4201 Coldwater Rd., Ste. P-05 Coldwater Rd., 4201, P-05 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-23 | COS | 2026-01-23 | COS | - | - |  |  | Variance Inspection | A grease trap/interceptor inspection performed Photos were sent of the grease traps empty. All components are in place in each grease trap |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-23 | COS | 2026-01-23 | COS | - | - |  |  | variance inspection | Monitoring point inspection Photos sent of the sampling ports installed. They look to be installed correctly |  | No
[4362] Shady Nook - 2834 Parnell Ave. Parnell Ave., 2834 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | - | Kirk Schmidt |  | Existing facility | Inspection to collect information or data about the facility FSE has a basement where the grease trap and sampling port could possibly be installed. FSE was instructed to have a licensed plumber install grease trap and sampling port. |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-09 | MAR | 2025-12-09 | MAR | - | - | Kirk Schmidt |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17535] Shigs In Pit - 6250 Maplecrest Rd. Maplecrest Rd., 6250 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-19 | COS | 2025-12-19 | COS | - | - |  |  | Investigation | Inspection to collect information or data about the facility manholes were frozen with landscaping over them. Will come back to inspect |  | No
[17535] Shigs In Pit - 6250 Maplecrest Rd. Maplecrest Rd., 6250 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | - | Heather Harrold |  | Existing facility | Inspection to collect information or data about the facility FSE was inspected after Sewer Maintenance found an issue in the sewer and traced it back to Shigs in Pit. Grease build up in the sanitary was the issue. IPS inspected and found the CMH to be ba |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | PASS - Passed Inspection | Heather Harrold |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Heather Harrold |  | Existing facility | Monitoring point inspection CMH was backed up with sanitary and grease |  | No
[17535] Shigs In Pit - 6250 Maplecrest Rd. Maplecrest Rd., 6250 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-23 | MAR | 2025-12-23 | MAR | - | - | Heather Harrold |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17870] Silverado Properties LLC - 4210-4226 Crescent Ave. Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-12 | MAR | 2026-02-12 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[17391] Sister Pho - 4210 Crescent Ave. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-03-09 | COS | 2026-03-09 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator traced the 3-basin. Will do additional testing if there is a problem in the future |  | No
[9243] Smokey Bones BBQ & Grill #7555 - 1203 Apple Glen Blvd. Apple Glen Blvd., 1203 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[9243] Smokey Bones BBQ & Grill #7555 - 1203 Apple Glen Blvd. Apple Glen Blvd., 1203 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-01 | MAR | 2026-04-01 | MAR | - | - | John Harper |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17606] Smoothie King #1522 - 1824 W. Dupont Rd. Ste. G Dupont Rd., W., 1824., Ste. G Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required | Regina Esparza |  | Existing facility | A grease trap/interceptor inspection performed Grease trap could not be opened. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | - |  |  | Existing facility | Monitoring point inspection CMH is shared with other tenants. CMH depth at center is 36" and 32" at edge. No usable step in place, set sampler in CMH |  | No
[17606] Smoothie King #1522 - 1824 W. Dupont Rd. Ste. G Dupont Rd., W., 1824., Ste. G Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | - | Regina Esparza |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17611] Solbird - 1824 W. Dupont Rd., Ste.A Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | - | Jerry Perez |  | Existing facility | Inspection to collect information or data about the facility FSE shares a CMH with Smoothie King who is in this multi tenant strip. |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[17611] Solbird - 1824 W. Dupont Rd., Ste.A Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH is 32" deep at the edge and 36" deep in the center with no usable step. Sampler can sit on bottom of CMH |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-04 | MAR | 2025-12-04 | MAR | - | - | Jerry Perez |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10027] Speedway No. 5161 - 6205 Illinois Rd. Illinois Rd., 6205 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-15 | MAR | 2025-09-15 | MAR | - | FUNC - Fully Functional |  |  | CMH Inspection | Monitoring point inspection Inspected CMH for backup - all clear. CMH depth is 78" and it is 35" to first step. |  | No
[17640] Speedway/Super America LLC #7071 - 8829 Coldwater Rd. Coldwater Rd., 8829 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-21 | MAR | 2025-10-21 | MAR/NSC | - | PASS - Passed Inspection |  |  | Existing Facility | Inspection to collect information or data about the facility A grease trap/interceptor inspection performed and a CMH inspection was performed |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-21 | MAR | 2025-10-21 | MAR/NSC | - | FUNC - Fully Functional |  |  | Existing Facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-21 | MAR | 2025-10-21 | MAR/NSC | - | FUNC - Fully Functional |  |  | Existing Facility | Monitoring point inspection |  | No
[9895] Spudz - 5428 New Haven Ave. New Haven Ave., 5428 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-08 | MAR | 2025-12-08 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility All food is served on Styrofoam plates and are thrown away, Food is cooked in an Auto fryer and the fry oil is taken out to a grease hopper. There is a Pizza oven. FSE has a hand sink, mop si |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-08 | MAR | 2025-12-08 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17645] Starbucks Coffee Company #10736 - 502 W. Jefferson Blvd. Jefferson Blvd., W., 502 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor needs pumped to verify center baffle |  | No
[17645] Starbucks Coffee Company #10736 - 502 W. Jefferson Blvd. Jefferson Blvd., W., 502 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9831] Starbucks Coffee Company #2526 - 4716 Illinois Rd. Ste. 103 Illinois Rd., 4716., Ste. 103 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[9831] Starbucks Coffee Company #2526 - 4716 Illinois Rd. Ste. 103 Illinois Rd., 4716., Ste. 103 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17586] Starbucks Coffee Company #51519 - 10104 Maysville Rd. Maysville Rd., 10104 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[17586] Starbucks Coffee Company #51519 - 10104 Maysville Rd. Maysville Rd., 10104 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-04 | MAR | 2026-03-04 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10260] Starbucks Coffee Company #9520 - 10030 Lima Rd. Lima Rd., 10030 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility This facility does not have a CMH |  | No
[10260] Starbucks Coffee Company #9520 - 10030 Lima Rd. Lima Rd., 10030 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1574] Steak-N-Shake #173 - 5303 Coldwater Rd. Coldwater Rd., 5303 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is overly full |  | No
[1574] Steak-N-Shake #173 - 5303 Coldwater Rd. Coldwater Rd., 5303 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Met the Waste Hauler Mahoney at the FSE and had the Grease Interceptor pumped. Center baffle and interior condition is functional. Mahoney does not jet so we will need to return at a later date to verify the |  | No
[1574] Steak-N-Shake #173 - 5303 Coldwater Rd. Coldwater Rd., 5303 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
[18481] Stop On The Way - Marathon (middle tenant) - 4619 Bass Rd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New Build | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator all kitchen fixtures to GI |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New Build | A grease trap/interceptor inspection performed functional condition with center baffle in place. Outlet tee/downleg missing Picture sent with new outlet tee/downleg installed 3.20.26 |  | No
[18481] Stop On The Way - Marathon (middle tenant) - 4619 Bass Rd. Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-11 | COS | 2026-03-11 | COS | - | - |  | Zachary Moorman | New Build | Monitoring point inspection Functional/new condition |  | No
[10139] Subway #15178 - 6807 Lima Rd. Lima Rd., 6807 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-06 | COS | 2025-11-06 | NSC | - | - |  |  |  | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-07 | NSC | 2025-11-06 | NSC | - | - |  |  | Gather Information | Facility has one 3-basin sink where generally washing is performed. Another washing sink (single basin) is present for pouring excess liquid out of jars/cans and for rinsing vegetables. There is no internal grease trap present and there does not appear to |  | Yes
[17654] Subway #2449 - 116 W. Rudisill Blvd. Ste. 102 Rudisill Blvd., W. 116, Ste. 102 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-05 | MAR | 2026-03-05 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-05 | MAR | 2026-03-05 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-05 | MAR | 2026-03-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10308] Subway #24991 - 10462 Maysville Rd. Maysville Rd., 10462 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Subway at 10462 Maysville Rd. has a 3 basin sink for cleaning and a 1 basin sink for food prep (veggie's and such). Will need to come back and dye trace to verify that the 3 basin goes to a sha |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[10325] Subway #29196/Sparky Mart in Shell - 11310 Old Decatur Rd. Old Decatur Rd., 11310 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE was found to have an External grease interceptor but was not able to be opened. A call was put in to maintenance manager to have grease interceptor opened and cleaned. Building owner is |  | No
[10325] Subway #29196/Sparky Mart in Shell - 11310 Old Decatur Rd. Old Decatur Rd., 11310 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Unable to open Grease Interceptor |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility FSE was scheduled to have the Grease Interceptor pumped and have the baffle verified. J&S was unable to open Grease Interceptor and had to reschedule for another day. CMH was found east of the |  | Yes
[10325] Subway #29196/Sparky Mart in Shell - 11310 Old Decatur Rd. Old Decatur Rd., 11310 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-12-31 | MAR | 2025-12-31 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-07 | COS | 2026-01-07 | COS | - | - |  | Mark A Rekeweg | Maint. Check | A grease trap/interceptor inspection performed they were able to get the lid off the grease interceptor. They had to bust the lid off so they replaced the manhole lid. The interceptor was in functional condition, except it was missing the outlet tee/down |  | No
[9570] TA Express - 3037 Goshen Rd. Goshen Rd., 3037 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-06 | COS | 2025-10-06 | COS | - | - |  |  | CMH Insp. | Monitoring point inspection Went to see if the Manhole listed in the facility's info was actually a CMH. I believe it is a shared manhole |  | No
[18464] Taco Bell - 405 W. Jefferson Blvd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-11-04 | COS | 2025-11-04 | COS | - | - |  | Mark A Rekeweg | New Build | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator all kitchen fixtures flow to GI |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-04 | COS | 2025-11-04 | COS | - | - |  | Mark A Rekeweg | New Build | A grease trap/interceptor inspection performed functional condition with center baffle and outlet tee/downleg in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-11-04 | COS | 2025-11-04 | COS | - | - |  | Mark A Rekeweg | New Build | Monitoring point inspection functional/new condition |  | No
[4209] Taco Bell #35391 - 4747 Coldwater Rd. Coldwater Rd., 4747 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-13 | MAR | 2026-01-13 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1195] Taco Bell #35394 - 3320 St. Joe Ctr. Rd. St. Joe Ctr. Rd., 3320 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Inspection to collect information or data about the facility CMH is 35" deep with one step off to the side. Sampler can be put directly in the hole. Grease Interceptor was nearly full. FSE employee was informed to look into having Grease Interceptor pum |  | Yes
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor is a one manhole model. FSE employee was informed that Grease Interceptor is close to being full and was recommended to have it pumped if it is not scheduled for in the near future. |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection CMH is 35" deep with one step off to the side. Sampler can be put directly in the hole. |  | No
[1195] Taco Bell #35394 - 3320 St. Joe Ctr. Rd. St. Joe Ctr. Rd., 3320 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-05 | MAR | 2026-01-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1735] Taco Bell #35401 - 2020 N. Coliseum Blvd. Coliseum Blvd., N., 2020 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor was overly full |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[1735] Taco Bell #35401 - 2020 N. Coliseum Blvd. Coliseum Blvd., N., 2020 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-02 | MAR | 2026-03-02 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-13 | COS | 2026-03-13 | COS | - | - |  | Zachary Moorman | Pumpout inspection | A grease trap/interceptor inspection performed functional condition with center baffle and outlet tee/downleg FOG content was a little above the center baffle. This could indicate settling or erosion has occurred. There may be a need to replace in the f |  | No
[10111] Taco Bell #35402 - 6608 Lima Rd. Lima Rd., 6608 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Could not see interior of Grease Interceptor to verify condition |  | No
[10111] Taco Bell #35402 - 6608 Lima Rd. Lima Rd., 6608 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-14 | MAR | 2026-01-14 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[10111] Taco Bell #35402 - 6608 Lima Rd. Lima Rd., 6608 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-04-09 | MAR | 2026-04-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[1172] Taco Bell #35411 - 3950 E. Dupont Rd. Dupont Rd., E., 3950 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[1172] Taco Bell #35411 - 3950 E. Dupont Rd. Dupont Rd., E., 3950 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-09 | MAR | 2026-02-09 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17369] Taco Bell #35413 - 1209 Reckeweg Rd. Reckeweg Rd., 1209 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | PASS - Passed Inspection |  |  | Existing facility | Monitoring point inspection |  | No
[17369] Taco Bell #35413 - 1209 Reckeweg Rd. Reckeweg Rd., 1209 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-03-19 | MAR | 2026-03-19 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[1259] Thai Diner Restaurant - 5129 Illinois Rd. Ste. 123 Illinois Rd., 5129 Ste 123 Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-07 | SJR | 2025-11-07 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | A dye trace to prove the monitoring point belongs to the facility Confirmed location of CMH shared by entire strip mall |  | No
[18358] Thai Garden - 10376 Leo Rd. Ste B Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-16 | COS | 2025-09-16 | MAR | - | - |  |  | Sampling event | Monitoring point inspection sampling port previously was floored over, but they exposed the sampling port so it can be sampled now |  | No
[10358] The Friendly Fox - 4001 S. Wayne Ave. Wayne Ave., S., 4001 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | - | Dan Saucer |  | Existing facility | Inspection to collect information or data about the facility FSE has a basement. The kitchen has a high temp dishwasher, hand sink, and a single basin for washing dishes. There are two single basin sinks out front on is by the coffee bar and one is by th |  | Yes
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-12-10 | MAR | 2025-12-10 | MAR | - | - | Dan Saucer |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[9777] The Grind - 4201 Coldwater Rd., Ste. D-03B Coldwater Rd., 4201, Ste. D-03B Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-02-06 | COS | 2026-02-06 | COS | - | - |  |  | DVS Request | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator 3-basin to GT |  | No
[9777] The Grind - 4201 Coldwater Rd., Ste. D-03B Coldwater Rd., 4201, Ste. D-03B Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2026-02-06 | COS | 2026-02-06 | COS | - | - |  |  | DVS request | A dye trace to prove the monitoring point belongs to the facility all fixtures except 3-basin to sanitary. They will be installing a sampling port |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-06 | COS | 2026-02-06 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed functional condition with all components in place |  | No
[9302] The Pantry - 1501 N. Wells St. Wells St., N., 1501 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-05 | MAR | 2025-11-05 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Facility was inspected for Grease trap and sampling port, neither were found. FSE was informed to have licensed plumber install Grease trap and sampling port. |  | No
[9302] The Pantry - 1501 N. Wells St. Wells St., N., 1501 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-05 | MAR | 2025-11-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[18447] The Pointe Church - 5335 Bass Rd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-06 | COS | 2025-10-06 | COS | - | - |  |  | Pre-Remodel | Inspection to collect information or data about the facility Inspection to determine remodel requirements. This facility has had many additions to it so the sewer lines may come out multiple different places of the building. There is a kitchen in the bas |  | No
[9386] The Rock Tavern - 1916 Broadway St. Broadway St., 1916 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - | April Fulk |  | Existing facility | Inspection to collect information or data about the facility Facility is a bar that only offers Pizza cooked with a Ninja and potatoes chips. No grease trap or sampling port. |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-10 | MAR | 2025-11-10 | MAR | - | - | April Fulk |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17438] Tim Horton's #5862 - 3975 Ice Way Ice Way., 3975 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2026-01-07 | COS | 2026-01-07 | COS | - | - |  | Brenda Stopher | Investigation | Inspection to collect information or data about the facility they had a blockage and will need to jet and camera the line to determine the issue. Will be sending a letter about the requirements and findings |  | No
[17438] Tim Horton's #5862 - 3975 Ice Way Ice Way., 3975 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-07 | COS | 2026-01-07 | COS | - | - |  | Brenda Stopher | Investigation | A grease trap/interceptor inspection performed the water level was lower than the outlet and the inlet indicating that there is a leak in the interceptor. They also have sewage in the interceptor due to a back flowing issue. They will need to pump and je |  | No
[17382] Union Social/Blind Tiger - 12628 Coldwater Rd. Coldwater Rd., 12628 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-09-30 | COS | 2025-09-30 | COS | - | - |  |  | Remodel | Inspection to collect information or data about the facility Union Social is on the main floor and Blind Tiger is in the basement which is on a different permit. Bling Tiger is not ready to be inspected yet. |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-09-30 | COS | 2025-09-30 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed Grease traps (2) need cleaned (required cleaning every two weeks) Keep log of cleanings Control manhole eligible for sampling. |  | No
[17382] Union Social/Blind Tiger - 12628 Coldwater Rd. Coldwater Rd., 12628 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-09-30 | COS | 2025-09-30 | COS | - | - |  |  | Remodel | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-13 | COS | 2025-11-13 | COS | - | - |  |  | Remodel | A grease trap/interceptor inspection performed basement GT was in functional condition |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-11-13 | COS | 2025-11-13 | COS | - | - |  |  | remodel | Outreach to a facility manager where an outreach binder is delivered & explained previously explained the packet, but went over cleaning frequency and other important notes |  | No
[18423] Valvoline - 6433 E. State Blvd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-09-12 | BSS | 2025-09-12 | BSS | - | PASS - Passed Inspection |  |  | New build | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-09-12 | BSS | 2025-09-12 | BSS | - | PASS - Passed Inspection |  |  | New Build | A dye trace to prove the monitoring point belongs to the facility |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-09-12 | BSS | 2025-09-12 | BSS | - | PASS - Passed Inspection |  |  | New build | Monitoring point inspection |  | No
[18423] Valvoline - 6433 E. State Blvd. Fort Wayne
| Inspection Oil/Sand Separator - An oil separator inspection performed |  |  | 2025-09-12 | BSS | 2025-09-12 | BSS | - | - |  |  | New Build | An oil separator inspection performed |  | No
[18441] Van Eerden Food Service - 8252 Smith Rd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-09-17 | BSS | 2025-09-17 | BSS | - | PASS - Passed Inspection |  |  | DVS New Build - | O/S @ Refrigeration Machine Room A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator | O/S @ Refrigeration Machine Room | No
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-09-17 | BSS | 2025-09-17 | BSS | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | DVS New Build | O/S @Maintenance Room A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator | O/S @Maintenance Room Line to O/S was plugged - Contractor needs to remove debris in plumbing line from Trench drain to O/S. | No
[18441] Van Eerden Food Service - 8252 Smith Rd. Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-09-17 | BSS | 2025-09-17 | BSS | - | PASS - Passed Inspection |  |  | DVS New Build | A dye trace to prove the monitoring point belongs to the facility |  | No
| Inspection Oil/Sand Separator - An oil separator inspection performed |  |  | 2025-09-17 | BSS | 2025-09-17 | BSS | - | PASS - Passed Inspection |  |  | DVS - New Build | O/S @ Refrigeration Machine Room An oil separator inspection performed | O/S @ Refrigeration Machine Room | No
| Inspection Oil/Sand Separator - An oil separator inspection performed |  |  | 2025-09-17 | BSS | 2025-09-17 | BSS | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | DVS New Build | O/S @Maintenance Room An oil separator inspection performed | O/S @Maintenance Room - Needs to be brought up to grade | No
[18441] Van Eerden Food Service - 8252 Smith Rd. Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-09-24 | BSS | 2025-09-24 | BSS | - | PASS - Passed Inspection |  |  | Follow-up - DVS New Build | O/S @Maintenance Room A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator | O/S @Maintenance Room | No
| Inspection Oil/Sand Separator - An oil separator inspection performed |  |  | 2025-09-24 | BSS | 2025-09-24 | BSS | - | PASS - Passed Inspection |  |  | Follow-up O/S - DVS New Build | O/S @Maintenance Room An oil separator inspection performed | O/S @Maintenance Room | No
[18444] W&S Asian Market LLC - 7511 S. Anthony Blvd. Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-03 | MAR | 2025-10-03 | MAR | - | PASS - Passed Inspection | Kar Sim |  | DVS Request - New FSE | Outreach to a facility manager where an outreach binder is delivered & explained Informed them that process changes may require additional requirements |  | No
[9923] Waynedale Café - 5700 Bluffton Rd. Bluffton Rd., 5700 Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-22 | COS | 2025-10-22 | COS | - | - |  |  | DVS request | Inspection to collect information or data about the facility facility is required to install a sampling port and to connect the prewash to the grease trap. They were given 120 days |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-22 | COS | 2025-10-22 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed functional condition. Has multiple baffles in place and an outlet downleg |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2025-10-22 | COS | 2025-10-22 | COS | - | - |  |  | DVS Request | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
[17897] Wing Stop - 5129 Illinois Rd. Ste. 126 Illinois Rd., 5129., Ste. 126 Fort Wayne
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-11-07 | SJR | 2025-11-07 | SJR | - | - |  | Mark A Rekeweg | Existing Facility | A dye trace to prove the monitoring point belongs to the facility Confirmed location of CMH shared by entire strip mall |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-01-22 | MAR | 2026-01-22 | COS | - | - |  | Mark A Rekeweg | Existing facility | A grease trap/interceptor inspection performed 2 manhole Grease trap |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-01-22 | MAR | 2026-01-22 | COS | - | PASS - Passed Inspection |  | Mark A Rekeweg | Existing facility | Monitoring point inspection Sampling port did show signs of build up |  | No
[17897] Wing Stop - 5129 Illinois Rd. Ste. 126 Illinois Rd., 5129., Ste. 126 Fort Wayne
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-01-22 | MAR | 2026-01-22 | COS | - | - |  | Mark A Rekeweg | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2026-03-25 | MAR | 2026-03-25 | MAR | - | - |  |  | Existing facility | Inspection to collect information or data about the facility Inspected FSE since it was reported that they had cleaned and pumped the Grease trap and sampling port. When I took a grab sample I noticed that the oil globules were still floating in circles, |  | No
[4206] Wu's Fine Chinese Cuisine - 4411 Coldwater Rd. Coldwater Rd., 4411 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  |  | Existing facility | A grease trap/interceptor inspection performed Grease Interceptor were overly full |  | No
[4206] Wu's Fine Chinese Cuisine - 4411 Coldwater Rd. Coldwater Rd., 4411 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
| Outreach - Outreach to a facility manager where an outreach binder is delivered & explained |  |  | 2026-02-05 | MAR | 2026-02-05 | MAR | - | - |  |  | Existing facility | Outreach to a facility manager where an outreach binder is delivered & explained |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | - |  |  | Existing facility | A grease trap/interceptor inspection performed |  | No
[4206] Wu's Fine Chinese Cuisine - 4411 Coldwater Rd. Coldwater Rd., 4411 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2026-03-23 | MAR | 2026-03-23 | MAR | - | - |  |  | Existing facility | Monitoring point inspection |  | No
[3072] Yahala Café - 6536 E. State Blvd. Fort Wayne
| Informational - Inspection to collect information or data about the facility |  |  | 2025-11-14 | COS | 2025-11-14 | COS | - | - |  |  | DVS Request | Inspection to collect information or data about the facility this facility is required to install a sampling port. It will be tricky because the grease traps are on opposite walls and a line would have to cross a walkway to get the grease traps to be plu |  | No
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-11-14 | COS | 2025-11-14 | COS | - | - |  |  | DVS Request | A grease trap/interceptor inspection performed both grease traps are in functional condition with all components in place |  | No
[9269] YWCA/Gratitude Catering - 1313 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1313 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-10-30 | COS | 2025-10-30 | COS | - | - |  | Noah Crouse | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator the 3-basin and 1 basin in the main kitchen flows to interceptor |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2025-10-30 | COS | 2025-10-30 | COS | - | - |  | Noah Crouse | existing facility | A dye trace to prove the monitoring point belongs to the facility pre-wash, high temp dishwasher, and mop sink to CMH. Prewash needs replumbed |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2025-10-30 | COS | 2025-10-30 | COS | - | - |  | Noah Crouse | Remodel | Inspection to collect information or data about the facility the prewash will need replumbed to the interceptor. There were also 4 kitchens which were not mentioned in the inspection request. Only the main kitchen was dye traced and the other kitchens wi |  | No
[9269] YWCA/Gratitude Catering - 1313 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1313 Fort Wayne
| Inspection FOG Extractor - A grease trap/interceptor inspection performed |  |  | 2025-10-30 | COS | 2025-10-30 | COS | - | - |  | Noah Crouse | Remodel | A grease trap/interceptor inspection performed functional/new condition with inlet and outlet tee/downlegs in place and center baffle in place |  | No
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-30 | COS | 2025-10-30 | COS | - | - |  | Noah Crouse | Remodel | Monitoring point inspection functional/new condition |  | No
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2025-11-03 | COS | 2025-11-03 | COS | - | - |  | Mark A Rekeweg | Remodel - follow up | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator the warming kitchen (1 basin dump sink) and the training kitchen (3basin sink) flows to the interceptor |  | No
[9269] YWCA/Gratitude Catering - 1313 W. Washington Ctr. Rd. Washington Ctr. Rd., W., 1313 Fort Wayne
| Dye Trace Extractor - A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator |  |  | 2026-02-04 | COS | 2026-02-04 | COS | - | - |  |  | Remodel | A dye trace to determine which kitchen fixtures flow to the grease trap, interceptor or oil/sand separator They had a 3-basin, 2 basin, prewash, hand sink and low temp dishwasher. The hand sink and 2-basin sink flow to grease and everything else goes to |  | No
| Dye Trace Monitoring Point - A dye trace to prove the monitoring point belongs to the facility |  |  | 2026-02-04 | COS | 2026-02-04 | COS | - | - |  | Mark A Rekeweg | Remodel | A dye trace to prove the monitoring point belongs to the facility 3-basin, prewash and dishwasher flow to CMH. They will be replumbing the 3-basin and pre-wash |  | No
| Informational - Inspection to collect information or data about the facility |  |  | 2026-02-04 | COS | 2026-02-04 | COS | - | - |  |  | Remodel | Inspection to collect information or data about the facility inspection for the rental kitchen. They had a 3-basin, 2 basin, prewash, hand sink and low temp dishwasher. The hand sink and 2-basin sink flow to grease and everything else goes to sanitary. T |  | No
[10312] Ziano's Italian Eatery - 10520 Maysville Rd. Maysville Rd., 10520 Fort Wayne
| Inspection Monitoring Point - Monitoring point inspection |  |  | 2025-10-27 | MAR | 2025-10-27 | MAR | - | FAIL - Failed Inspection - structures need cleaned/pumped, lines need flushed, plumbing issue, repair or replacement required, follow-up required |  | Noah Crouse | Existing facility | Monitoring point inspection CMH backed up with grease. FSE was asked to have Extractor and CMH cleaned and jetted. |  | No